## Buses
Buses | CR Type | AC/DC | Status | Base kV | Area | Zone | Device Code | Bus Rating (A) | Design Capacity | Bus Bracing (kA) | Material | Dn Conn kVA | Dn Conn FLA | Dn Demand kVA | Dn Demand FLA | Dn Code kVA | Dn Code FLA | Future Conn kVA | Future Conn FLA | Future Demd kVA | Future Demd FLA | Future Code kVA | Future Code FLA | AF Type | AF Solution | Forced To | AF Option | AF Output | Working Distance Setting | Working Distance (in) | Electrode Gap (mm) | Electrode Configuration | Enclosure Height (in) | Enclosure Width (in) | Enclosure Depth (in) | Stored AFB (in) | Stored AF IE (cal/cm2) | Stored AF PPE | SC Sym kA | Label Comment | # Labels to Print | Facility | Location Name | Location Description | X | Y | Floor | Unavailable | Unavailable Reason | Data Status | Comment | Fault Current Angle
BUS_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
BUS_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL1_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL1_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL2_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL2_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL3_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL3_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL4_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL4_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL5_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL5_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL6_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL6_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL7_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL7_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL8_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL8_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL9_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL9_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL10_A |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL10_B |  | AC | On | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL_EQV |  | AC | Off | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
COL_EQV2 |  | AC | Off | 34.5 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 31 | 254 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV1_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV1_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV2_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV2_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV3_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV3_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV4_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV4_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV5_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV5_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV6_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV6_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV7_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV7_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV8_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV8_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV9_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV9_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV10_A |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV10_B |  | AC | On | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
INV_EQV |  | AC | Off | 0.69 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 32 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
STATION SERVICE |  | AC | On | 13 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 153 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
STATION SERVICE_A |  | AC | Off | 13 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Calculated |  | TCC | <<Use Global Option>> | Default | 18 | 153 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
UTIL |  | AC | On | 230 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Excluded |  |  | <<Use Global Option>> | Default | 63 | 342.9 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated
UTIL_A |  | AC | Off | 230 | 1 | 1 |  |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other | Excluded |  |  | <<Use Global Option>> | Default | 63 | 342.9 | VCB | [8 empty] | 1 | [6 empty] | No |  | Estimated

## Utilities
Utilities | CR Type | AC/DC | Status | To bus | Base kV | Util kV (LL) | Fault Unit | 3Ph SC1 | 3Ph SC2 | SLG SC1 | SLG SC2 | Model | MW | MVAR | Ctl kV pu | MVAR Min | MVAR Max | kV pu Min | kV pu Max | Ctl Angle | Ctl Bus | Ctl Base kV | R1 pu | X1 pu | R0 pu | X0 pu | Hrm RC Factor | Hrm RC Value | I Hrm Rating | Data Status | Comment
UTIL-1 |  | AC | On | UTIL | 230 | 230 | MVA | 25000 | 17 | 20000 | 17 | Swing | 0 | 0 | 1 | -100000 | 100000 | 0.8 | 1.2 | 0 | UTIL | 230 | 2.3e-05 | 0.000399 | 4.1e-05 | 0.000699 | R-EXP | 0.5 | 25.102 | Estimated
UTIL-1_A |  | AC | Off | UTIL_A | 230 | 230 | MVA | 25000 | 17 | 20000 | 17 | Swing | 0 | 0 | 1 | -100000 | 100000 | 0.8 | 1.2 | 0 | UTIL_A | 230 | 2.3e-05 | 0.000399 | 4.1e-05 | 0.000699 | R-EXP | 0.5 | 25.102 | Estimated

## Generators
Generators | CR Type | AC/DC | Status | To bus | Base kV | Gen kV (LL) | Conn | Rating | Rating Unit | Type | Power Factor | Efficiency | RPM | X/R | Model | MW | MVAR | Ctl kV pu | MVAR Min | MVAR Max | kV pu Min | kV pu Max | Ctl Angle | Ctl Bus | Ctl Base kV | X''dv | X'dv | X0 | Xlr | RG Ohm | XG Ohm | R1 pu | X1 pu | R0 pu | X0 pu | R Gnd pu | X Gnd pu | Hrm RC Factor | Hrm RC Value | I Hrm Rating | IEC RG (Ohms) | IEC pG | IEC RGf / X"d | Xd | T''d | T'd | Ta | Field Forcing pu | Damage I^2t pu | Facility | Location Name | Location Description | X | Y | Floor | Data Status | Comment
GEN-10_A |  | AC | On | INV10_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV10_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-10_B |  | AC | On | INV10_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV10_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-1_A |  | AC | On | INV1_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV1_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-1_B |  | AC | On | INV1_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV1_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-2_A |  | AC | On | INV2_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV2_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-2_B |  | AC | On | INV2_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV2_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-3_A |  | AC | On | INV3_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV3_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-3_B |  | AC | On | INV3_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV3_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-4_A |  | AC | On | INV4_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV4_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-4_B |  | AC | On | INV4_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV4_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-5_A |  | AC | On | INV5_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV5_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-5_B |  | AC | On | INV5_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV5_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-6_A |  | AC | On | INV6_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV6_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-6_B |  | AC | On | INV6_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV6_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-7_A |  | AC | On | INV7_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV7_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-7_B |  | AC | On | INV7_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV7_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-8_A |  | AC | On | INV8_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV8_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-8_B |  | AC | On | INV8_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV8_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-9_A |  | AC | On | INV9_A | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV9_A | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-9_B |  | AC | On | INV9_B | 0.69 | 0.69 | YG | 2.2 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 2 | 0 | 1 | -0.66 | 0.66 | 0.8 | 1.2 | 0 | INV9_B | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.1757 | 4.545 | 0.1757 | 4.545 | 0 | 0 | R-EXP | 0.5 | 1840.8 |  | 0 | [13 empty] | Estimated
GEN-EQV |  | AC | Off | INV_EQV | 0.69 | 0.69 | YG | 44 | MVA | SYN-SPA | 0.8 | 0.95 | 3600 | 25.866 | PV | 40 | 0 | 1 | -13.2 | 13.2 | 0.8 | 1.2 | 0 | INV_EQV | 0.69 | 100 | 100 | 100 |  | 0 | 0 | 0.0088 | 0.2273 | 0.0088 | 0.2273 | 0 | 0 | R-EXP | 0.5 | 36816.5 |  | 0 | [13 empty] | Estimated

## 2W-Xformers
2W-Xformers | CR Type | Status | From bus | From Base kV | From Conn | To bus | To Base kV | To Conn | IEC Conn Type | Unit | Type | Class | Temp | Form | Design | From Nom kV | From Tap kV | From Gnd R | From Gnd jX | To Nom kV | To Tap kV | To Gnd R | To Gnd jX | MVA | MVA O/L | Z | Z0 | X/R | X0/R0 | Loss (kW) | LTC Tap | LTC Step | LTC Min Tap | LTC Max Tap | Ctl Type | Ctl Value | Zps R1 pu | Zps X1 pu | Zps R0 pu | Zps X0 pu | Rps0+3Rpsg | Xps0+3Xpsg | From Gnd R1 pu | From Gnd jX pu | To Gnd R1 pu | To Gnd jX pu | IEC pT | TCC Standard | TCC FLA Based On | Freq Fault Curve | TCC Max Plot Time | TCC Inrush FLA Mult | TCC Inrush Cycles | Hrm RC Factor | Hrm RC Value | Hrm Pec-r % | Hrm From I Rating | Hrm To I Rating | Data Status | Comment
TX-10_A |  | On | COL10_A | 34.5 | D | INV10_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-10_B |  | On | COL10_B | 34.5 | D | INV10_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-1_A |  | On | COL1_A | 34.5 | D | INV1_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-1_B |  | On | COL1_B | 34.5 | D | INV1_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-2_A |  | On | COL2_A | 34.5 | D | INV2_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-2_B |  | On | COL2_B | 34.5 | D | INV2_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-3_A |  | On | COL3_A | 34.5 | D | INV3_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-3_B |  | On | COL3_B | 34.5 | D | INV3_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-4_A |  | On | COL4_A | 34.5 | D | INV4_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-4_B |  | On | COL4_B | 34.5 | D | INV4_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-5_A |  | On | COL5_A | 34.5 | D | INV5_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-5_B |  | On | COL5_B | 34.5 | D | INV5_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-6_A |  | On | COL6_A | 34.5 | D | INV6_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-6_B |  | On | COL6_B | 34.5 | D | INV6_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-7_A |  | On | COL7_A | 34.5 | D | INV7_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-7_B |  | On | COL7_B | 34.5 | D | INV7_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-8_A |  | On | COL8_A | 34.5 | D | INV8_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-8_B |  | On | COL8_B | 34.5 | D | INV8_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-9_A |  | On | COL9_A | 34.5 | D | INV9_A | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated
TX-9_B |  | On | COL9_B | 34.5 | D | INV9_B | 0.69 | Y |  | ANSI | Oil | OA | 65 | Core | (default) | 34.5 | 34.5 | 0 | 0 | 0.69 | 0.69 | 0 | 0 | 2.3 |  | 5.75 | 5.75 | 10 |  |  | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.0249 | 0.2488 | 1000 | 1e+06 | 1000 | 1e+06 | 0 | 0 | 0 | 0 |  | ANSI C57.109 | MVA O/L | Yes | 500 | 8 | 6 | R-EXP | 0 | 15 | 38.49 | 1924.5 | Estimated

## 3W-Xformers
3W-Xformers | CR Type | Status | Pri Bus | Pri Base kV | Pri Conn | Sec Bus | Sec Base kV | Sec Conn | Ter Bus | Ter Base kV | Ter Conn | Unit | Type | Class | Temp | Form | Pri Nom kV | Pri Tap kV | Pri MVA | Pri MVA O/L | Pri Gnd R | Pri Gnd jX | Sec Nom kV | Sec Tap kV | Sec MVA | Sec MVA O/L | Sec Gnd R | Sec Gnd jX | Ter Nom kV | Ter Tap kV | Ter MVA | Ter MVA O/L | Ter Gnd R | Ter Gnd jX | LTC1 Tap | LTC1 Step | LTC1 Min Tap | LTC1 Max Tap | LTC1 Ctl Type | LTC1 Ctl Value | LTC2 Tap | LTC2 Step | LTC2 Min Tap | LTC2 Max Tap | LTC2 Ctl Type | LTC2 Ctl Value | Zps R1 | Zps X1 | Zps R0 | Zps X0 | Zpt R1 | Zpt X1 | Zpt R0 | Zpt X0 | Zst R1 | Zst X1 | Zst R0 | Zst X0 | Zp-n R1 pu | Zp-n X1 pu | Zps R0 pu | Zps X0 pu | Rpn0+3Rpg | Xpn0+3Xpg | Zs-n R1 pu | Zs-n X1 pu | Zpt R0 pu | Zpt X0 pu | Rsn0+3Rsg | Xsn0+3Xsg | Zt-n R1 pu | Zt-n X1 pu | Zst R0 pu | Zst X0 pu | Rtn0+3Rtg | Xtn0+3Xtg | Pri Gnd R1 pu | Pri Gnd jX pu | Sec Gnd R1 pu | Sec Gnd jX pu | Ter Gnd R1 pu | Ter Gnd jX pu | TCC Standard | TCC FLA Based On | TCC Plot Side | Freq Fault Curve | TCC Max Plot Time | TCC Inrush FLA Mult | TCC Inrush Cycles | Hrm RC Factor | Hrm RC Value | Hrm Pec-r % | Hrm Pri I Rating | Hrm Sec I Rating | Hrm Ter I Rating | Data Status | Comment
MPT |  | On | UTIL | 230 | YG | BUS_A | 34.5 | YG | STATION SERVICE | 13 | D | ANSI | Oil | OA/FOA/FOA | 65 | Core | 230 | 230 | 50 | 83.33 | 0 | 0 | 34.5 | 34.5 | 50 | 83.33 | 0 | 0 | 13 | 13 | 20 | 33.33 | 0 | 0 | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.1 | 10 | 0.085 | 8.5 | 0.06 | 6 | 0.06 | 6 | 0.05 | 5.3 | 0.085 | 4 | 3.5e-05 | 0.0027 | 0.00017 | 0.017 | -6.8e-05 | 0.0045 | 0.000165 | 0.0172 | 1000 | 1e+06 | 0.000238 | 0.0125 | 8.5e-05 | 0.0093 | 1000 | 1e+06 | 0.000188 | 0.0075 | 0 | 0 | 0 | 0 | 0 | 0 | ANSI C57.109 | MVA O/L | Secondary | Yes | 500 | 8 | 6 | R-EXP | 0.5 | 15 | 125.511 | 836.74 | 888.231 | Estimated
MPT_A |  | Off | UTIL_A | 230 | YG | COL_EQV | 34.5 | YG | STATION SERVICE_A | 13 | D | ANSI | Oil | OA/FOA/FOA | 65 | Core | 230 | 230 | 50 | 83.33 | 0 | 0 | 34.5 | 34.5 | 50 | 83.33 | 0 | 0 | 13 | 13 | 20 | 33.33 | 0 | 0 | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | None | 0.625 | 0.001 | 1500 | V (PU) | 1 | 0.1 | 10 | 0.085 | 8.5 | 0.06 | 6 | 0.06 | 6 | 0.05 | 5.3 | 0.085 | 4 | 3.5e-05 | 0.0027 | 0.00017 | 0.017 | -6.8e-05 | 0.0045 | 0.000165 | 0.0172 | 1000 | 1e+06 | 0.000238 | 0.0125 | 8.5e-05 | 0.0093 | 1000 | 1e+06 | 0.000188 | 0.0075 | 0 | 0 | 0 | 0 | 0 | 0 | ANSI C57.109 | MVA O/L | Secondary | Yes | 500 | 8 | 6 | R-EXP | 0.5 | 15 | 125.511 | 836.74 | 888.231 | Estimated

## HV Breakers
HV Breakers | CR Type | Status | On Bus | Base kV | Conn Type | Normal State | Manufacturer | Type | Style | Cont Current (A) | SC Test Std | Cycles | C&L/Crest kA | Max kV | Rated kA @ Max kV | K-factor | Int kA | kA Min | kA Max | IEC Rated kV | IEC Making kA | IEC Opening Time (s) | IEC Breaking kA | IEC DC Time Const (s) | PCC kVA Demand | PCC Isc/ILoad | Data Status | Comment
BH-1 |  | On | BUS_A | 34.5 | Feeder | Closed | <None> | <None> | <None> | 0 | ANSI-SYM | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [7 empty] | Estimated
BH-1_A |  | Off | COL_EQV | 34.5 | Feeder | Closed | <None> | <None> | <None> | 0 | ANSI-SYM | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [7 empty] | Estimated

## Switches
Switches | CR Type | Status | On Bus | Base kV | Conn Type | Normal State | Manufacturer | Type | Style | Cont Current (A) | SC Mom kA | IEC Peak Withstand kA | SC Test Std | PCC kVA Demand | PCC Isc/ILoad | Data Status | Comment
S-2 |  | On | BUS_B | 34.5 | Bus Tie | Closed | <None> | <None> | <None> | 0 | 0 |  | ANSI-SYM |  |  | Estimated

## Cables
N | MW | From Bus ID | From Base kV | To Bus ID | To Base kV | Length | R1 | X1 | R0 | X0 | Xc | Xc0 | B1 | B2 | R1 | X1 | R0 | X0 | B1 | B0 | R1*MW^2 | X1*MW^2 | R0*MW^2 | X0*MW^2 | B1 | B0 | Duct Config | Spacing | R1 pu | X1 pu | R0 pu | X0 pu | B1 pu | B0 pu | IEC Field Temp(C) | IEC SC Temp(C) | IEC R1 Cmax pu | IEC R0 Cmax pu | IEC R1 Cmin pu | IEC R0 Cmin pu | Rating at Max Temp | Hrm RC Factor | Hrm RC Value | I Hrm Rating | Data Status | Comment
4 | 8 | COL1_A | 34.5 | COL2_A | 34.5 | 1000 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 27.1739 | 27.1739 | 5.8816 | 2.816 | 11.7632 | 5.6384 | 27.1739 | 27.1739 |  | 0 | 0.000772 | 0.00037 | 0.0015 | 0.00074 | 0.0032 | 0.0032 | 50 | 250 | 0.000679 | 0.0014 | 0.0014 | 0.0028 | 142 | R-EXP | 0.5 | 255 | Estimated
3 | 6 | COL2_A | 34.5 | COL3_A | 34.5 | 500 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.04595 | 0.022 | 0.0919 | 0.04405 | 13.587 | 13.587 | 1.6542 | 0.792 | 3.3084 | 1.5858 | 13.587 | 13.587 |  | 0 | 0.000386 | 0.000185 | 0.000772 | 0.00037 | 0.0016 | 0.0016 | 50 | 250 | 0.00034 | 0.000679 | 0.000695 | 0.0014 | 142 | R-EXP | 0.5 | 255 | Estimated
2 | 4 | COL3_A | 34.5 | COL4_A | 34.5 | 500 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.04595 | 0.022 | 0.0919 | 0.04405 | 13.587 | 13.587 | 0.7352 | 0.352 | 1.4704 | 0.7048 | 13.587 | 13.587 |  | 0 | 0.000386 | 0.000185 | 0.000772 | 0.00037 | 0.0016 | 0.0016 | 50 | 250 | 0.00034 | 0.000679 | 0.000695 | 0.0014 | 142 | R-EXP | 0.5 | 255 | Estimated
1 | 2 | COL4_A | 34.5 | COL5_A | 34.5 | 500 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.04595 | 0.022 | 0.0919 | 0.04405 | 13.587 | 13.587 | 0.1838 | 0.088 | 0.3676 | 0.1762 | 13.587 | 13.587 |  | 0 | 0.000386 | 0.000185 | 0.000772 | 0.00037 | 0.0016 | 0.0016 | 50 | 250 | 0.00034 | 0.000679 | 0.000695 | 0.0014 | 142 | R-EXP | 0.5 | 255 | Estimated
4 | 8 | COL6_A | 34.5 | COL7_A | 34.5 | 1000 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 27.1739 | 27.1739 | 5.8816 | 2.816 | 11.7632 | 5.6384 | 27.1739 | 27.1739 |  | 0 | 0.000772 | 0.00037 | 0.0015 | 0.00074 | 0.0032 | 0.0032 | 50 | 250 | 0.000679 | 0.0014 | 0.0014 | 0.0028 | 142 | R-EXP | 0.5 | 255 | Estimated
3 | 6 | COL7_A | 34.5 | COL8_A | 34.5 | 500 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.04595 | 0.022 | 0.0919 | 0.04405 | 13.587 | 13.587 | 1.6542 | 0.792 | 3.3084 | 1.5858 | 13.587 | 13.587 |  | 0 | 0.000386 | 0.000185 | 0.000772 | 0.00037 | 0.0016 | 0.0016 | 50 | 250 | 0.00034 | 0.000679 | 0.000695 | 0.0014 | 142 | R-EXP | 0.5 | 255 | Estimated
2 | 4 | COL8_A | 34.5 | COL9_A | 34.5 | 500 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.04595 | 0.022 | 0.0919 | 0.04405 | 13.587 | 13.587 | 0.7352 | 0.352 | 1.4704 | 0.7048 | 13.587 | 13.587 |  | 0 | 0.000386 | 0.000185 | 0.000772 | 0.00037 | 0.0016 | 0.0016 | 50 | 250 | 0.00034 | 0.000679 | 0.000695 | 0.0014 | 142 | R-EXP | 0.5 | 255 | Estimated
1 | 2 | COL9_A | 34.5 | COL10_A | 34.5 | 500 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.04595 | 0.022 | 0.0919 | 0.04405 | 13.587 | 13.587 | 0.1838 | 0.088 | 0.3676 | 0.1762 | 13.587 | 13.587 |  | 0 | 0.000386 | 0.000185 | 0.000772 | 0.00037 | 0.0016 | 0.0016 | 50 | 250 | 0.00034 | 0.000679 | 0.000695 | 0.0014 | 142 | R-EXP | 0.5 | 255 | Estimated
6 | 12 | COL1_B | 34.5 | COL2_B | 34.5 | 1000 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 27.1739 | 27.1739 | 13.2336 | 6.336 | 26.4672 | 12.6864 | 27.1739 | 27.1739 |  | 0 | 0.000772 | 0.00037 | 0.0015 | 0.00074 | 0.0032 | 0.0032 | 50 | 250 | 0.000679 | 0.0014 | 0.0014 | 0.0028 | 142 | R-EXP | 0.5 | 255 | Estimated
7 | 14 | COL2_B | 34.5 | COL3_B | 34.5 | 1000 | 0.0391 | 0.0392 | 0.0783 | 0.0784 | 0.0288 | 0.0288 | 34.7222 | 34.7222 | 0.0391 | 0.0392 | 0.0783 | 0.0784 | 34.7222 | 34.7222 | 7.6636 | 7.6832 | 15.3468 | 15.3664 | 34.7222 | 34.7222 |  | 0 | 0.000329 | 0.000329 | 0.000658 | 0.000659 | 0.0041 | 0.0041 | 50 | 250 | 0.000289 | 0.000579 | 0.000592 | 0.0012 | 236 | R-EXP | 0.5 | 425 | Estimated
8 | 16 | COL3_B | 34.5 | COL4_B | 34.5 | 1000 | 0.0391 | 0.0392 | 0.0783 | 0.0784 | 0.0288 | 0.0288 | 34.7222 | 34.7222 | 0.0391 | 0.0392 | 0.0783 | 0.0784 | 34.7222 | 34.7222 | 10.0096 | 10.0352 | 20.0448 | 20.0704 | 34.7222 | 34.7222 |  | 0 | 0.000329 | 0.000329 | 0.000658 | 0.000659 | 0.0041 | 0.0041 | 50 | 250 | 0.000289 | 0.000579 | 0.000592 | 0.0012 | 236 | R-EXP | 0.5 | 425 | Estimated
9 | 18 | COL4_B | 34.5 | COL5_B | 34.5 | 1000 | 0.0391 | 0.0392 | 0.0783 | 0.0784 | 0.0288 | 0.0288 | 34.7222 | 34.7222 | 0.0391 | 0.0392 | 0.0783 | 0.0784 | 34.7222 | 34.7222 | 12.6684 | 12.7008 | 25.3692 | 25.4016 | 34.7222 | 34.7222 |  | 0 | 0.000329 | 0.000329 | 0.000658 | 0.000659 | 0.0041 | 0.0041 | 50 | 250 | 0.000289 | 0.000579 | 0.000592 | 0.0012 | 236 | R-EXP | 0.5 | 425 | Estimated
4 | 8 | COL6_B | 34.5 | COL7_B | 34.5 | 1000 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 27.1739 | 27.1739 | 5.8816 | 2.816 | 11.7632 | 5.6384 | 27.1739 | 27.1739 |  | 0 | 0.000772 | 0.00037 | 0.0015 | 0.00074 | 0.0032 | 0.0032 | 50 | 250 | 0.000679 | 0.0014 | 0.0014 | 0.0028 | 142 | R-EXP | 0.5 | 255 | Estimated
3 | 6 | COL7_B | 34.5 | COL8_B | 34.5 | 1000 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 27.1739 | 27.1739 | 3.3084 | 1.584 | 6.6168 | 3.1716 | 27.1739 | 27.1739 |  | 0 | 0.000772 | 0.00037 | 0.0015 | 0.00074 | 0.0032 | 0.0032 | 50 | 250 | 0.000679 | 0.0014 | 0.0014 | 0.0028 | 142 | R-EXP | 0.5 | 255 | Estimated
2 | 4 | COL8_B | 34.5 | COL9_B | 34.5 | 1000 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 27.1739 | 27.1739 | 1.4704 | 0.704 | 2.9408 | 1.4096 | 27.1739 | 27.1739 |  | 0 | 0.000772 | 0.00037 | 0.0015 | 0.00074 | 0.0032 | 0.0032 | 50 | 250 | 0.000679 | 0.0014 | 0.0014 | 0.0028 | 142 | R-EXP | 0.5 | 255 | Estimated
1 | 2 | COL9_B | 34.5 | COL10_B | 34.5 | 1000 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0919 | 0.044 | 0.1838 | 0.0881 | 27.1739 | 27.1739 | 0.3676 | 0.176 | 0.7352 | 0.3524 | 27.1739 | 27.1739 |  | 0 | 0.000772 | 0.00037 | 0.0015 | 0.00074 | 0.0032 | 0.0032 | 50 | 250 | 0.000679 | 0.0014 | 0.0014 | 0.0028 | 142 | R-EXP | 0.5 | 255 | Estimated
10 | 20 | BUS_A | 34.5 | COL1_A | 34.5 | 500 | 0.0268 | 0.0441 | 0.107 | 0.1765 | 0.0288 | 0.0288 | 34.7222 | 34.7222 | 0.0134 | 0.02205 | 0.0535 | 0.08825 | 17.3611 | 17.3611 | 5.36 | 8.82 | 21.4 | 35.3 | 17.3611 | 17.3611 |  | 0 | 0.000112 | 0.000185 | 0.00045 | 0.000741 | 0.0021 | 0.0021 | 50 | 250 | 9.9e-05 | 0.000396 | 0.000202 | 0.000809 | 261 | R-EXP | 0.5 | 470 | Estimated
5 | 10 | COL1_A | 34.5 | COL6_A | 34.5 | 1000 | 0.0559 | 0.0506 | 0.2235 | 0.2024 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0559 | 0.0506 | 0.2235 | 0.2024 | 27.1739 | 27.1739 | 5.59 | 5.06 | 22.35 | 20.24 | 27.1739 | 27.1739 |  | 0 | 0.000469 | 0.000425 | 0.0019 | 0.0017 | 0.0032 | 0.0032 | 50 | 250 | 0.000413 | 0.0017 | 0.000845 | 0.0034 | 161 | R-EXP | 0.5 | 290 | Estimated
10 | 20 | BUS_B | 34.5 | COL5_B | 34.5 | 500 | 0.0268 | 0.0441 | 0.107 | 0.1765 | 0.0288 | 0.0288 | 34.7222 | 34.7222 | 0.0134 | 0.02205 | 0.0535 | 0.08825 | 17.3611 | 17.3611 | 5.36 | 8.82 | 21.4 | 35.3 | 17.3611 | 17.3611 |  | 0 | 0.000112 | 0.000185 | 0.00045 | 0.000741 | 0.0021 | 0.0021 | 50 | 250 | 9.9e-05 | 0.000396 | 0.000202 | 0.000809 | 261 | R-EXP | 0.5 | 470 | Estimated
5 | 10 | COL1_B | 34.5 | COL6_B | 34.5 | 1000 | 0.0559 | 0.0506 | 0.2235 | 0.2024 | 0.0368 | 0.0368 | 27.1739 | 27.1739 | 0.0559 | 0.0506 | 0.2235 | 0.2024 | 27.1739 | 27.1739 | 5.59 | 5.06 | 22.35 | 20.24 | 27.1739 | 27.1739 |  | 0 | 0.000469 | 0.000425 | 0.0019 | 0.0017 | 0.0032 | 0.0032 | 50 | 250 | 0.000413 | 0.0017 | 0.000845 | 0.0034 | 161 | R-EXP | 0.5 | 290 | Estimated
| Total MW | [19 empty] | Total
| 40 | [19 empty] | 93.4128 | 77.8912 | 230.6032 | 211.3872 | 464.9758 | 464.9758
Equivalent
[21 empty] | 0.058383 | 0.048682 | 0.14413 | 0.13212 | 0.0021506 | 0.0021506